## Sheet1
MERCY CORPS NIGERIA
SPECIFICATIONS FOR SOLAR MODULES (COMITAS PROGRAM)
Key Features
Cell Type | Monocrystalline
Efficiency | >= 19%
Wind load | >=2400 Pascals
Product Warranty | 10Years minimum
Performance Warranty | 25 Years linear power production,
Maximum annual performance degradation | Maximum 0.8% per year, to produce at least 80% of rated power at Year 25
Front glass features | Tempered glass with High transmission, Low iron
Electrical
Connection | TUV 1z4.0mm2 of at least 900mm length with low-smoke, and fire-retardant protection.
Reverse-pole protection | Forward-biased diode protection between terminals
Junction box | Minimum IP67 rating
Power rating | xxxxWp
Maximum system voltage | 1000Vdc
Power Tolerance | 4%
Nominal operating cell temperature | 45 +- 2oC`
Certifications
ISO | ISO9001:2008
ISO14001:2004
OHSAS18001
Standards | IEC61215
IEC61730