## Sheet1
MERCY CORPS NIGERIA |  |  | CONTRACTOR'S NAME
THE BILL OF QUANTITIES FOR THE PROPOSED CONSTRUCTION OF THE INFILTRATION GALLERY, STEEL STANCHION, FETCHING POINTS, SOLARIZATION AND PERIMETER FENCING AT GWEILA COMMUNITY - SHELLENG WARD, SHELLENG LGA.
ELEMENT 1: PRELIMINARY AND GENERAL
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL (NGN.)
Allow for the following general items
a | Demolitions and site preparations
b | Foreman - in - charge and Quality Assurance / Control
c | mobilization and final demobilization after completion
d | Plant, Tools, and Equipment
e | Temporary Scaffolding
f | Watching, temporary hoarding, Site Administration and Security
g | Temporary lighting and Power
h | Temporary office accommodation for Contractor/Consultants & Site meetings |  |  | ,
i | Temporary accommodation for workmen
j | Safety, Health, Welfare, First Aid Equipment, Planked Footway, Construction Design and Management (CDM) Coordinator and Protection of works
k | Water supply for the Works , scaffolding
l | Setting out
m | Programme of works and Progress Photographs
n | Removal of rubbish, debris, all surplus material / hazardous materials and their containers and spoil at least once every week , more frequently if necessary, and keep the site and works clean and tidy. Retain waste transfer documentation on site
o | Cleaning out on Completion
p | Samples and Testing for civil works ( slump test on site and cube test)
q | Bonds and Insurances
| Total for preliminaries and general carried to summary |  |  |  | 0
ELEMENT 2: INFILTRATION GALLERY CONSTRUCTION AND DEVELOPMENT.
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL (NGN.)
Pre-Installation and hydrogeological investigation
| Carry out pre-drilling hydrogeological investigation as specified (with confirmation report submitted) Water quality test. | LS | 1 |  | 0
1 | SITE CLEARING AND MOBILIZATION
a | Mobilization of drilling and excavation machine and necessary tools, equipment to site, erecting,dismantling and demobilize upon completion | Item | 1 |  | 0
2 | WELL EXCAVATION AND GALLERY TRENCH EXCAVATION
a | Obtaining not less than 4 feet diameter circular and square culvert internal diameter well, and cubic area excavation of 6.0x6.0m x 15m Using cutters, manual excavators, machines, and other equipment to burrow a well and galLery plane, through all sorts of strata. Protection of caving by supplying necessary surface casing or retaining materials, and collection of soil samples at every 2m or every change of strata and preserving them for analysis, withdrawal of boring & casing pipes etc. NOTE: PAYMENTS SHALL BE MADE AS PER THE ACTUAL ACTUAL AREA EXCAVATED. | m3 | 550 |  | 0
| Gallery lanscapping and bed sieve preparation | m3 | 36 |  | 0
| Gallery Screen Casing Installations (6nos.) of 3meters each panar of 15 Bar. | M | 6 |  | 0
| Sub Total |  |  |  | 0
3 | WELL LINNING
a | Supply and installation of 4-foot diameter reinforced concrete circular or square culvert rings. | M | 10 |  | 0
b | 4 Bags of Cement and requisite concrete materials for blocking the pipe ends and other dressings | No | 4 |  | 0
4 | GRAVEL PACKING
a | Provide of suitable gravel pack to fill the annular space between the sides of the the screen. The gravel pack grain sizes should range from 2-3 mm in diameter. Reasonably homogenous, calibrated, clean from debris, round and preferably siliceous available from the riverbed, free from soil and other materials, including supply, delivery, casting and cleaning. Enough gravel pack shall be installed to completely cover the uppermost screen and yonder by an additional 2-metres to allow for settling. A good supply of water should be introduced with the gravel to prevent bridging. | LS | 2 |  | 0
5 | GROUTING
a | Grouting with a mixture of sharp sand , cement and gravel The first clay grout of 2 meters length must be placed on top of the gravel pack to stop the grout from plugging the gravel pack. Including supply, delivery, fitting and fixing. Install a perimeter casting of 1.5foot around the gallery. | M | 44 |  | 0
6 | GALLERY PIT DEVELOPMENT
a | The service provider shall carry out development and cleaning of bored wel by consistent discharge by use of irrigation pumps for 3 hrs upon completion of installation of concrete rings and gravel packing. This shall be done to remove silts, clays and fluid residues deposited in well and on the wallsl . | Item | 1 |  | 0
7 | GALLERY WELL TEST PUMPING
a | Establish borehole parameters by test pumping the Gallery well for 12 hours and provide well data such as yield, draw-down, Dynamic/Static water level, etc. The following elements will be contained in the test pumping. a) A period of recovery after production pumping/development. b) A pre-test (calibration, typically 2 to 3 hours); c) A period of recovery after the pre-test d) A step draw-down test e) A period of recovery after the step draw-down test Refer to test pumping report form for other required data. | LS | 1 |  | 0
8 | WATER QUALITY TEST
a | A minimum of 2 litres each for chemical and bacteriological analysis shall be collected by the contractor in the presence of the Engineer or his representative. (3) Water samples should be collected in clean, sterilized properly sealed and protected plastic containers from the borehole for reference to a Water Testing Authority recognized and authorized by Mercy Corps for laboratory analysis, after completion of test pumping. One sample will be used for each of these tests: physical, chemical and bacteriological analyses. The samples so collected should reach the authorized Water Testing Laboratories (Ministry of Water Resources and National Agency for Food and Drug Law and Control (NAFDAC)), within 6 hours from the time of collection from the borehole unless otherwise. Specific parameters to be measured shall include. • Physical Parameters – Colour, Odour, Taste, Turbidity, pH Value, Electrical Conductivity, Temperature • Chemical Parameters – Nitrate, Nitrite, Total Hardness, Fluoride, Chloride, Sulphate, Copper, Manganese, TDS, Total Iron, Arsenic • Biological Parameters – Faecal Coli form Counts | LS | 1 |  | 0
9 | INFILTRATION GALLERY COMPLETION REPORT
a | A full Infiltration Gallery completion report shall be prepared by the service provided and submitted to the Mercy Corps within five days of the completion of the pumping tests. The borehole completion report shall include the following: a. A borehole log, showing borehole location, ground surface elevation, measuring point elevation, soil strata, static water level and dimensions of casing, screen position within the well height, grounding, and cap. b. Pumping test reports c. Result of analysis of water d. All other records as specified | Report | 1 |  | 0
10 | INFILTRATION GALLERY CLEANING AND DISINFECTION
a | Provide for the disinfection of well by introducing granular Calcium Hypochlorite or Sodium Hypochlorite into the annular space along with the gravel pack material at a concentration of 500grammes per cubic meter of pack. | LS | 1 |  | 0
11 | SANITARY SEAL AND CAPPING
a | To provide an effective perimeter block wall around the well and reinforced concrete slab seal of 0.9m above the block wall to cover the well, block wall should above the ground level to prevent the entry of contaminants, up to 1.50 meters depth of the well from the surface shall be grouted using a concrete mix of 1:2:4 there shall be a 1.5m x 1.5m x 2m concrete slab. | LS | 1 |  | 0
| Sub Total for Borehole Drilling Carried to Summary |  |  |  | 0
ELEMENT 3: INSTALLATION OF SUBMERSIBLE BOREHOLE PUMP AND SOLARIZATION
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL (NGN.)
ALL PROVISIONAL:
NOTE:The pump selection and associated accessories subject to change based on the Gallery yield
The actual pump specs to be determined upon drilling and test pumping. Please take note that the pump may be changed and cost varied to suit the borehole specifications
1 | Pump Installation
a | Supply and Installation of hybrid Groundfus SQ Flex2.5-2 Pump | pcs | 1 |  | 0
b | Supply and Installation of Grundfos CU200 Control Unit | pcs | 1 |  | 0
c | Supply materials, fabricate and fix protector/casing for CU200 Control switch | pcs | 1 |  | 0
d | Supply and Installation of 380 watts, 24V (nominal) mono-crystalline solar panels. Recommended canadian solar, JA, Jinko or approved equivallent. The type, size, brand of the solar panel to be supplied MUST comply to the solar specifications in the annex and MUST be pre-approved before purchase and delivery to site for installation. | Pcs | 6 |  | 0
e | Supply and install DC Surge protector of 1000v (Schnider) including all its connecting accessories | pcs | 1 |  | 0
f | Supply and install Groundfos SQF (GF-100) float switch or equivalent including all connecting accessories and cables | Ls | 1 |  | 0
g | Supply and installation of 4mm 4 core flat submersible cable to connect pump from installation depth to ground level | m | 20 |  | 0
h | Supply and installation of 6mm 2 core PV cable from solar panels to CU200 control unit | m | 10 |  | 0
i | Supply and Installation of full 6mm 3 core armoured cable from ground level to CU200 control unit. | meter | 10 |  | 0
n | Supply and Installation of 10mm Marine safety rope | Bundle | 1 |  | 0
p | Supply and Installation of foreign Indian riser pipes 3m length 1¼" with UPVC Sockets | pcs | 6 |  | 0
3 | Flow Meter and Manual chlorine feeder
a | Masonry or blockwork chamber ,clear opening 1000mm X 1000mm, in 225mm blockwork filled solid in C10/20 concrete, depth n.e. 1.5 m. Include for lockable precast cover slabs in100mm thick sections | Ls | 1 |  | 0
b | Supply and install Automatic Chemical Feeder (chlorine) with Mounting Base Hayward CL200 or equal approved equivalent: with complete plumbing accessories and UPVC Adaptors with provision for a by-pass connection) | Ls | 1 |  | 0
c | Supply and install water flow meter with all plumbing accessories | pcs | 1 |  | 0
d | Allow for construction of a masonry chamber 2150 x 1050mm raised 1m above ground level to house the chlorine feeder and water meter | pcs | 1 |  | 0
| Sub-Total |  |  |  | 0
4 | H channel: 127x76mm x 8kg/m , 75x75x6mm angle steel frame work for Solar rack on the elevated steel tower welded, and grinded joints, including paintings to engineers detailed design and specifications in:
a | Frame that will accommodate 6 - 8 -PV panels | Ls | 1 |  | 0
b | Bracing of frame using angle steel | Ls | 1 |  | 0
c | Apply 2 coats of red oxide to protect the frame from corrosion | Ls | 1 |  | 0
d | Apply 3 coat of Alluminium paint to all surface of constructed frame | Ls | 1 |  | 0
| Sub- Total |  |  |  | 0
| Sub total for Gallery Excavation carried to summary |  |  |  | 0
ELEMENT 4: 6M HIGH STEEL TOWER & INSTALLATION OF 2N0.5,000L PVC TANK- LABRIJEIJEI COMMUNITY SHELLENG WARD, ADAMAWA, STATE
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL (NGN.)
1 | Sub-structure (All Provisional)
a | Excavate for foundation to a depth of 2000m and cart away excavated material | m3 | 8.8405 |  | 0
b | Backfill selected excavated material; well consolidated in 150mm layers around foundation and level the entire area | m3 | 5.3043 |  | 0
2 | Supply materials, prepare and cast PCC concrete grade M15 (1:2:4 - 20mm aggregate in:
a | Blinding layers (1:3:6) | m3 | 0.288 |  | 0
3 | Supply materials, prepare and cast reinforced concrete grade M20 (1:1.5:3 - 20mm aggregate) with Y20 @ 200mm c/c. (Price includes steel reinforcement and formwork. Refer to technical specification for more details) in:
a | Foundation footing | m3 | 2.592 |  | 0
b | Beams | m3 | 0.9675 |  | 0
c | Columns | m3 | 2 |  | 0
0
4 | Super structure (Steel Works and Tanks)
Elevated Steel Tower welded, and grinded joints, including paintings to engineers detailed design and specifications (Pri. Beam H channel: 203x102x23kg/m, Angle iron: 60x60x5mm, U channel: 100x50mm x 10kg/m, Sec. beam H channel: 127x76mm x 8kg/m
a | Fabrication and mounting of steel members for water reservoir. Refer and follow technical specification, manufactures instructions, site instructions, approved scope of work and working drawings. | Ls | 1 |  | 0
5 | Installation of steel plate platform, ladders, level indicator, hand rails and piping as per drawings. Refer and follow technical specification and approved scope of work.
a | Provide and install Galvanize steel grating 30mm for all platform including walkway as specified in the design | M2 | 16 |  | 0
b | Install a ladder to the walkways station and access to solar panels using 60x60x5mm angle steel and SHS40X40X4MM for steps, 50x5mm thick flat bar for belt, including additional bracing. | Ls | 1 |  | 0
c | Supply and install 5000L PVC GEEPEE Tank or its equivalent with all fittings and accessories including union couplings at tank outlets and control valves on each tank. Allow for plumbing works (inlet, outlet, overflow all connected to ground level) | pcs | 2 |  | 0
d | Allow for plumbing works of the pvc tanks inter-connected to form one inlet and outlet (NOTE: inlet, outlet, overflow pipes all connected to ground level) | LS | 1 |  | 0
Security light
e | 600watts aston solar street light with motion sensor, coverage distance - 24m, charging time (4-6hrs), working time (12-24hrs), minimum battery capacity | Nr | 1 |  | 0
f | Supply steel plate material and inscribe the project and logo as directed by MCN personel. The visibility board (8ft x 4 feet) to be mounted on the walk way support structure above the stanchion. | pcs | 1 |  | 0
| Total for 6M high steel tower and installation of 2No. 5,000L pvc tank at Filin Hujji Vet site |  |  |  | 0
ELEMENT 5: PERIMETER FENCING
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL (NGN.)
a | Excavate trench not exceeding (0.6mx0.6mx40m perimeter) to receive block work as foundation | M3 | 14.4 |  | 0
b | excavate pits to receive concrete for columns at the 4 corners of perimeter fence n.e 1m | M3 | 1.2 |  | 0
c | Backfill and ram foundation spread and remove surplus excavated materials | M3 | 15.12 |  | 0
d | concrete coulmns to four sides of perimeter fence | m3 | 4 |  | 0
d | Plain In-situ concrete (concrete mix – 1:2:4 – 20mm aggregate) in: Foundation (blinding) (0.6mx0.05mx40m) | M3 | 1.2 |  | 0
e | 9" hollow sandcrete block work bedded and jointed in cement and sand mortar (mix 1:6) as foundation lining (0.25x3mx.40m) | M2 | 30 |  | 0
f | 100 X50 X8.3KG/M IPE welded on a base plate of 12mm thickness of 300mmx300mm and installed on the four corners of perimeter fence with a HDB and nut of 20 mm | Pcs | 2 |  | 0
g | Supply and install 50 x 50 x2.5mm SHS Pipes placed in between IPE columns @ 2m c/c around the perimeter fence | Pcs | 16 |  | 0
h | supply and install 50x50x2.5mm SHS Square pipes braced round the fence area as shown in the drawings | pcs | 4 |  | 0
h | 60mmx60mmx5mm angle iron welded to steel columns along the perimeter of the fence. | pcs | 6 |  | 0
i | Apply Red oxide as 2 coats to protect the steel columns from corrosion. | Ls | 1 |  | 0
j | Apply 3 coat of Alluminium paint to all surface of constructed frame | Ls | 2 |  | 0
k | A142 Wire mesh 6mm welded to the SHS Ppes and IPE columns around the fence perimeter resting on the the top of the laid foundation block wall 40 m perimeter and jointed to block by 2 inches plaster | M2 | 73.8 |  | 0
l | Razor fence galvanized barb wire installed along the entire 40m perimeter inclusive of metal anchorage, "Y" | M | 32 |  | 0
m | 600watts aston solar street light including necessary installation accessories, complete with steel pole stand and concrete footing. | No | 1 |  | 0
n | Supply and spread 10m³ sharp sand within the borehole perimeter and fetching point. | trip | 2 |  | 0
o | Purpose made steel door with accessories fixed to square pipe column to provide entry and exit with dimension 2mx2m | Ls | 1 |  | 0
P | Landscape fenced area and finish with 1/2'' granite chippings | tonnes | 30 |  | 0
Q | Emulsion Paint light Ash for perimeter wall (perimeter wall) | No. | 1 |  | 0
| Sub total for perimeter fencing |  |  |  | 0
ELEMENT 5: CONSTRUCTION OF ONE FETCHING POINT & A SOAK AWAY PIT
ITEM | DESCRIPTION | UNIT | QTY | RATE | TOTAL (NGN)
1 | Secondary network distribution using but not limited to: PVC 11/2" -1" Tee connector, PVC 11/2" -1" 90 degrees elbow, PVC 1" pipe, PVC reducer 11/2" x ¾", GI faucet ¾" high quality tap heads, 0.2m ¾ flexible hose and clip on tap heads to mitigate spillage, PVC elbow 1"-¾", Teflon tape (thread tape), 2" PVC socket, PVC pipe 2" 6m long, 2"-11/2" PVC reducer
a | Allow for the supply and reticulation of water from water source to one fetching point including all connecting asscessories and materials and or tools not limited to PVC pipes, valves, reducers, tap heads, elbows, Teflon tapes souckets, reducers, Union including trench excavation not less than 0.6m for laying pipe 11/2" , pipes reticulating water to a distance not exceeding 100m away from the elevated tanks. | Ls | 1 |  | 0
| Sub- Total |  |  |  | 0
3 | Concrete work-water Point
a | Excavation | m3 | 2.8 |  | 0
b | Foundation in two courses of 9" sandcrete block | m2 | 19 |  | 0
c | Concrete blinding (ratio 1:2:4) 50mm thickness | m3 | 2.5 |  | 0
d | Plastering/Rendering of surface/ flooring (ratio 1:4) 20mm thickness | m3 | 2.5 |  | 0
e | Pipe installations: Supply and install 10m 1¼" UPVC pipes & fittings laid in block work of fetching point and 6m ¾" UPVC pipes and fittings with 12 nos GI Taps | LS | 1 |  | 0
f | Block work to house Taps (Fetching points) | m2 | 5.58 |  | 0
g | Tiles | LS | 1 |  | 0
| Sub- Total |  |  |  | 0
4 | Soak Pit
a | Excavation | m3 | 9.5 |  | 0
b | Blinding in excavated pit (ratio 1:5) 50mm thickness | m3 | 0.2 |  | 0
c | Pit lining with 9" sandcrete blocks | pcs | 19.5 |  | 0
d | Backfill and compact | m3 | 1.2 |  | 0
e | UPVC pipe 4" | pcs | 2 |  | 0
f | 4" PVC Union | pcs | 1 |  | 0
g | PVC Elbow 4" 90 degrees | pcs | 1 |  | 0
i | Precast concrete service slab (400x400x75mm) | m3 | 0.12 |  | 0
j | Precast concrete service slab (1500x1500x100mm) | m3 | 0.225 |  | 0
k | 12mm reinforecement @150 c/c for all precast slabs | m | 1.5 |  | 0
l | Anchor for service slab 8mm tensile steel rod | pcs | 2 |  | 0
m | 2"x 3" hard sawn wood for formwork | m | 10 |  | 0
n | Plastering of surfaces above ground level and two course below ground level 50mm thick (ratio 1:4) | m2 | 8.4 |  | 0
Hardcore as described
o | Allow for hardcore filling with hard non-absorbable hardcore including levelling and consolidating in 150mm layers soak pit | m3 | 5 |  | 0
| Sub-Total fetching point/Reticulation |  |  |  | 0
5 | Animal Trough
a | Excavation for all trough areas | m3 | 10.9 |  | 0
b | 6mm reinforcemnet bars @300c/c | m | 47 |  | 0
c | Concrete work 1.2.4 ratio laid on reinforecemnt on all trough floor and walls areas | m3 | 20.5 |  | 0
d | sawn form work of marine boards to specification as shown in drawings | m2 | 8 |  | 0
| Sub-Total -Animal Trough |  |  |  | 0
6 | Secondary network distribution using but not limited to: PVC 11/2" -1" Tee connector, PVC 11/2" -1" 90 degrees elbow, PVC 1" pipe, PVC reducer 11/2" x ¾", GI faucet ¾" high quality tap heads, 0.2m ¾ flexible hose and clip on tap heads to mitigate spillage, PVC elbow 1"-¾", Teflon tape (thread tape), 2" PVC socket, PVC pipe 2" 6m long, 2"-11/2" PVC reducer
a | Reticulation (500meters) | ls | 1 |  | 0
| SUMMARY TOTAL |  |  |  | 0